## Slide 1: LESSONS LEARNED FROM REAL WORLD EVENTS
HOSPITAL EMERGENCY MANAGEMENT
MAY 8, 2024
LOUISIANA EMERGENCY MANAGEMENT CONFERENCE

## Slide 2: Willis Knighton Health (WKH) has served the Northwest Louisiana communities since 1924. WKH is accredited through The Joint Commission and has four emergency departments that serve the Shreveport/Bossier City area, eight urgent care centers, over 100 clinics/physician services, cancer treatment center with the only proton treatment therapy available in the state, and four fitness/wellness centers. Our mission-”to continuously improve the health and well-being of the people we serve.”

## Slide 4: Disasters and Emergencies have a tremendous impact on hospital systems like WKH. These include Natural Disasters such as tornados, flooding, extreme winter weather; Accidental Disasters such as utility failures, fire, train derailment; and Intentional Events such as active shooter/killer, cyberattacks, workplace violence, and terrorism.

## Slide 5
Disasters and Emergencies
Winter Storm Event- February 2021
Extreme Cold Temperature Event- December 2022
Tornado Event- March 2023
“Derecho” Severe Weather Event- June 2023
Winter Storm Event- January 2024

## Slide 6
Winter Weather Event-February 2021
February 15-25, 2021
Six inches of snow and sleet
Record low temperature set
Rolling blackouts by AEP/SWEPCO to conserve the electrical grid due to demand
Multiple Water Main breaks throughout the city causing loss of complete pressure in system.

## Slide 7
Temperatures and Precipitation

## Slide 8
Challenges From the Event
Prolonged days of sub-freezing temperatures
Lack of Back-Up Plans
Loss of city water pressure due to water main breaks
Could not perform dialysis
Damaged Property & Sanitary Issues
Ambulance ER driveways iced over
Discharging patients from the hospitals
No travel resources- taxis, uber, funeral homes
Lack of Hospital Incident Command System (HICS)
Staffing shortages due to travel hazards
Once water pressure returned-boil advisory in place until water tested.

## Slide 9
Lessons Learned and Mitigation
Water Supply- wells were dug at each major hospital for non-potable resources.
Bottled Water Supply maintained and contracts in place to continue supply as needed.
Port-a-lets had to be used at all facilities; tank type toilets added to public restrooms so they can be flushed with bucket brigade.
Booster pumps were added to each hospital to boost lost pressure needed to continue dialysis.
Heaters were added to ER driveways and Ice Melt provided by vendor.
Community partners assisted getting patients home and staff back and forth to hospital to meet mission.
Needed to provide better overnight accommodations for staff.
Add ICS 100 and 200 for all potential staff to fill HICS positions.
Our ESF-8 DRC for Region 7 does an annual HICS class each year.
Two temporary morgues established now in Caddo Parish.

## Slide 10
Extreme Cold Temperatures- December 2022
December 23-30, 2022
Lowest temperature in 2022 recorded was 10⁰ on December 23, 2022.
Temperatures below freezing for 44 hours
Record setting wind chill at -5⁰
Fortunately, we had no snow, sleet, ice, or freezing rain with this event.

## Slide 11
Challenges From the Event
Extended period of sub-freezing temperatures and record setting wind chills.
Wells froze up before we started flowing water
Loss of city water pressure again due to water main breaks when temperatures rose to high 30s and the thaw began.
Dialysis Operations hindered again.
Event occurred during scheduled holidays for health system- Christmas Eve and Christmas Day.
Boil Advisory after pressure restored again hindered daily hospital operations.

## Slide 12
Lessons Learned and Mitigation
Our wells froze up due to extreme cold temperatures. Now we have protected closures, protected lines and start flowing water from wells before freezing temps arrive.
One hospital well was found to have high iron content and water resource had to be provided for HVAC system. New well to be dug.
There were no elective surgeries scheduled. However, ED operations and patient care on floors had to continue.
Bucket Brigade for toilets supplemented Port-a-lets.
Added low pressure water alarm for each hospital.
Due to expected high level of dialysis needs the day after Christmas, dialysis contingency plan was developed to transfer patients to WK hospital in Bossier.
Booster pumps were able to provide enough pressure to continue dialysis in Shreveport.
Future Project--Self-sustaining potable water supply for main hospital.

## Slide 13
Tornado Event- March 2, 2023
EF-1 Tornado
Caddo Parish Sheriff’s Office confirmed tornado on the ground at approximately 1800 hours.
Damaged the Oaks of Louisiana-Dependent Living, Assisted Living, and Skilled Nursing Facility Campus.
Damaged five businesses and multiple homes heavily damaged.
No injuries or deaths reported.

## Slide 14
Challenges From the Event
NWS reported “The tornado was referred to as a low topped storm, not like a typical tall thunderstorm. This caused a weaker rotation and more difficulty to spot the signs on the NWS radar.” – Charlie Woodrum, NWS Meteorologist.
Was not initially detected and confirmed on radar by NWS Shreveport delaying the tornado warning.
NOAA Weather Radios needed updating.
Recovery of some damages was prolonged.
No Tornado Sirens on the property.

## Slide 15
Video of March 2, 2023, Shreveport Tornado
Chart: 

## Slide 16
Tornado Damage to Oaks Property

## Slide 17
Lessons Learned and Mitigation
Notification needs addressed
  New NOAA radios programmed for the zip code
  Residents were encouraged to turn on Emergency Alerts and Public Safety Alerts notifications on their cell phones.
  Residents were educated on local resources for notification through “Everbridge” registration of their phone with Caddo Office of Homeland Security and Emergency Preparedness.
  Tornado Sirens are being researched now.
Residents and staff members have recurring education on “Code Grey Warning” response.
Tornado Drills are performed more often; with special emphasis on the primary (Spring) and secondary (November/December) severe weather seasons in Northwest Louisiana.
Prolonged recovery on removing tree debris and clearing property. Consider having contracts in place for this.

## Slide 18
“Derecho” Severe Weather Event
June 16, 2023
Approximately 0130 hours
Derecho- is a widespread, long-lived windstorm that is associated with a band of rapidly moving showers or thunderstorms. Destruction is like a tornado, but in one direction along a relatively straight path.-National Weather Service.
At one point 233,898 AEP/SWEPCO customers were without power.
Widespread tree and property damage and power lines down.

## Slide 20
Challenges From the Event
Wind blew the roof off the ICU unit at one hospital prompting life safety measures to relocate them to a safe area.
Three of the four hospitals were without power for 36-48 hours and over half the clinics were without power.
Greatly affected ER operations. Only Level One Trauma Center closed temporarily. Messaging to community. (PIO)
Heat and humidity buildup in hospital were significant.
Some critical sources not on generator power (Red Plugs).
Main Server Room overheated causing several systems to shutdown.
Fuel resources became an issue for generators and transport.
Surgeries and Cath Lab Canceled. No MRI or CT due to heat and no alternative cooling method.
Loss of refrigerated medications and vaccines.

## Slide 21
Lessons Learned and Mitigation
Test all red plugs (generator powered plugs) to ensure they are working properly. Add more red plugs for critical equipment.
Future project- generator to power all critical services at our primary hospital.
Booster pumps added to generator power.
Push notifications to IT staff when server room temperatures are approaching shutdown thresholds.
Additional temperature monitoring and cooling methods for server rooms, CT, MRI, and Lab.
Recognized the critical need to ensure we had a functional PIO capable of messaging critical information to the community.
Created Microsoft TEAMS command group for messaging out IAP, SitRep, and other command communications up and down the chain.
Area Hospital collaboration, communication and contingency planning when outages affect ER and Hospital capabilities creating more limited and complete diversions.
Plan is now in place to ensure all perishable meds and vaccines are relocated in refrigerators on generator plug power.
Re-committed fuel contracts for generators and plan for maintenance to stay abreast of fuel status. Fuelman locations with city of Shreveport departments were confirmed and MOU to utilize.

## Slide 22
Winter Weather Storm Event- 2024
January 14-20, 2024
Extended hours of sub-freezing temperatures
Sleet and Freezing Rain Event
Primarily sleet accumulation up to and over one inch.
One positive was not a big freezing rain event and had no loss of power at hospitals.

## Slide 23
Challenges from the Event
Hospital Command Center needed updating from IT, power needs, and communication.
Clinic supervisory staff did not get needed communications.
Staffing shortages due to hazardous road conditions.
Some staff stayed overnight at hospitals-lodging & food service.
Facility parking lots were very hazardous and not all treated.
Complete loss of water pressure at one hospital and low pressure at all others.
Boil Advisory affected hospital- sterile processes, dialysis, ice machines.
Booster pumps would cavitate and shut down.

## Slide 24
Lessons Learned and Mitigation
IT will update primary command center with power, phones, and two more monitors for briefings and command meetings.
All HCC should be stood up during system wide events.
Utilize Send Word Now for mass communication messaging to staff. Core group of physician services supervisor added to TEAMS command group.
WK staff and resources requested through local OHSEP office provided transportation to and from the hospital for staff that could not drive safely. Liability-??
Chief Nursing Officers would like to be more active in their individual command centers for their assigned hospital staffing and resource needs.
Developing an app or electronic means for staff to request lodging and food service if staying overnight at hospital.
We needed to confirm water & ice supply contracts and work towards securing our own self-sustaining water supply (looking at military water storage bladders).
Contract vendor to supply and apply ice melt to all major hospital parking lots.
Infection Prevention and Control developing a boil advisory policy to solidify elements of re-processing: Sterile processing for surgeries and GI Lab upper and lower procedure probes.
Option of conducting our own water quality testing confirmed by LDH Engineer to continue water usage.

## Slide 25
Closing and Final Thoughts
Relationships- local, state, federal, unified command group
Preparedness- drills, exercises (discussion and operational), workshops, webinars, and organizational recurring education
“You will perform how you prepare.”
Situational Awareness
Engage your Hospital Leadership
Be a student of your profession
“Perfection does not exist—you can always do better, and you can always grow.”- Les Brown

## Slide 26: Thank You!! Scott Wolverton swolverton@wkhs.com 318-212-4025